## Sheet1
COMPARISON OF December 2012 FINAL to December 2011 Reproposal and FINAL March 2011 BOILER MACT LIMITS and June 2010 PROPOSED BOILER MACT LIMITS
HAP/Fuel | Proposal | Final | Re-proposal | 2012-12-01 | Factor Better | Proposal | Final | Re-proposal | 2012-12-01 | Factor Better | Units | Output Based (lb/MMBtu steam output) - March 2011 to Dec 2012
| Existing Boilers |  |  |  |  | New Boilers | [5 empty] | Existing | 2012-12-01 | New | 2012-12-01
Hg Biomass | 0.9 | 4.6 | 3.1 | 5.7 | 1.8387 | 0.2 | 3.5 | 0.86 | 0.8 | 0.93023 | lb/TBtu | 4.5 | 6.4 | 3.4 | 0.87
PM Biomass | 0.02 | 0.039 | multiple | multiple | below | 0.008 | 0.0011 | multiple | multiple | NA | lb/MMBtu | 0.038 | multiple | 0.0011 | multiple
HCl Biomass | 0.006 | 0.035 | 0.022 | 0.022 | 1 | 0.004 | 0.0022 | 0.022 | 0.022 | 1 | lb/MMBtu | 0.04 | 0.025 | 0.0021 | 0.025
Hg Coal | 3 | 4.6 | 3.1 | 5.7 | 1.8387 | 2 | 3.5 | 0.86 | 0.8 | 0.93023 | lb/TBtu | 4.5 | 6.4 | 3.4 | 0.87
PM Coal | 0.02 | 0.039 | multiple | multiple | below | 0.001 | 0.0011 | multiple | multiple | below | lb/MMBtu | 0.038 | multiple | 0.0011 | multiple
HCl Coal | 0.02 | 0.035 | 0.022 | 0.022 | 1 | 6e-05 | 0.0022 | 0.022 | 0.022 | 1 | lb/MMBtu | 0.04 | 0.025 | 0.0021 | 0.025
Hg Oil | 4 | 3.5 | 26 | 2 | 0.076923 | 0.3 | 0.21 | 0.49 | 0.48 | 0.97959 | lb/TBtu | 3.3 | 2.5 | 0.2 | 0.53
Hg Oil non-continental | 4 | 0.78 | 26 | 2 | 0.076923 | 0.3 | 0.78 | 0.49 | 0.48 | 0.97959 | lb/TBtu | 0.8 | 2.5 | 0.8 | 0.53
PM Oil | 0.004 | 0.0075 | multiple | multiple | below | 0.002 | 0.0013 | multiple | multiple | NA | lb/MMBtu | 0.0073 | multiple | 0.001 | multiple
HCl Oil | 0.0009 | 0.00033 | 0.0012 | 0.0011 | 0.91667 | 0.0004 | 0.0032 | 0.0012 | 0.00044 | 0.36667 | lb/MMBtu | 0.003 | 0.0014 | 0.003 | 0.00048
Hg Gas 2 | 0.2 | 13 | 7.9 | 7.9 | 1 | 0.2 | 7.9 | 7.9 | 7.9 | 1 | lb/TBtu | 7.8 | 14 | 0.2 | 14
PM Gas 2 | 0.05 | 0.043 | 0.0067 | 0.0067 | 1 | 0.003 | 0.0067 | 0.0067 | 0.0067 | 1 | lb/MMBtu | 0.026 | 0.012 | 0.004 | 0.012
HCl Gas 2 | 3e-06 | 0.0017 | 0.0017 | 0.0017 | 1 | 3e-06 | 0.0017 | 0.0017 | 0.0017 | 1 | lb/MMBtu | 0.001 | 0.0029 | 0.003 | 0.0029
Or clean gas 2 can opt in to Gas 1 work practice if: | NA | Hg content <40 ug/m3 |  |  |  | NA | Hg content <40 ug/m3
Short-term/3 hour test | Existing Boilers |  |  |  |  | New Boilers | [5 empty] | Existing | 2012-12-01 | New | 2012-12-01
CO Biomass Wet Stoker/Sloped Grate/Other | 560 | 490 | 790 | 1500 | 1.8987 | 560 | 160 | 590 | 620 | 1.0508 | ppm at 3%O2 | 0.35 | 1.4 | 0.13 | 0.58
CO Biomass Kiln-Dried Stoker/Sloped Grate/Other | 560 | 490 | 250 | 460 | 1.84 |  | 160 | 250 | 460 | 1.84 | ppm at 3%O2 |  | 0.42 |  | 0.42
CO Biomass FB | 250 | 430 | 370 | 470 | 1.2703 | 40 | 260 | 230 | 230 | 1 | ppm at 3%O2 | 0.28 | 0.46 | 0.18 | 0.22
CO Biomass Dutch/Pile | 1010 | 470 | 810 | 770 | 0.95062 | 1010 | 470 | 810 | 330 | 1.7234 | ppm at 3%O2 | 0.45 | 0.84 | 0.45 | 0.35
CO Biomass Suspension Burner | 1010 | 470 | 58 | 2400 | 41.3793 | NA | NA | 58 | 2400 | NA | ppm at 3%O2 | 0.45 | 1.9 | 0.45 | 1.9
CO Biomass Fuel Cell | 270 | 690 | 1500 | 1100 | 0.73333 | 270 | 470 | 210 | 910 | 4.3333 | ppm at 3%O2 | 0.34 | 2.4 | 0.23 | 1.1
CO Biomass Hybrid Suspension/ Grate | NA | 3500 | 3900 | 2800 | 0.71795 | NA | 1500 | 1500 | 1100 | 0.73333 | ppm at 3%O2 | 2 | 2.8 | 0.84 | 1.4
CO Coal pulverized | 90 | 160 | 41 | 130 | 3.1707 | 90 | 12 | 9 | 130 | 14.4444 | ppm at 3%O2 | 0.14 | 0.11 | 0.01 | 0.11
CO Coal stoker | 50 | 270 | 220 | 160 | 0.72727 | 7 | 6 | 19 | 130 | 6.8421 | ppm at 3%O2 | 0.25 | 0.14 | 0.005 | 0.12
CO Coal FB | 30 | 82 | 56 | 130 | 2.3214 | 30 | 18 | 17 | 130 | 7.6471 | ppm at 3%O2 | 0.08 | 0.12 | 0.02 | 0.11
CO Coal FBHE |  |  |  | 140 |  |  |  |  | 140 |  |  |  | 0.13 |  | 0.12
CO Oil - Heavy | 1 | 10 | 10 | 130 | 13 | 1 | 3 | 10 | 130 | 13 | ppm at 3%O2 | 0.0083 | 0.13 | 0.0026 | 0.13
CO Oil - Light | 1 | 10 | 7 | 130 | 18.5714 | 1 | 3 | 3 | 130 | 43.3333 | ppm at 3%O2 | 0.0083 | 0.13 | 0.0026 | 0.13
CO Oil non-continental | 1 | 160 | 18 | 130 | 7.2222 | 1 | 51 | 18 | 130 | 7.2222 | ppm at 3%O2 | 0.13 | 0.13 | 0.043 | 0.13
CO Gas2 | 1 | 9 | 4 | 130 | 32.5 | 1 | 3 | 4 | 130 | 32.5 | ppm at 3%O2 | 0.005 | 0.16 | 0.002 | 0.16
Long-term CEMS limit (30 day avg except as noted) |  |  |  | 30 day except as noted |  |  |  |  | 30 day except as noted
CO Biomass Wet Stoker/Sloped Grate/Other | NA | NA | 410 | 720 | 1.7561 | NA | NA | 410 | 390 | 0.95122 | ppm at 3%O2
CO Biomass Kiln-Dried Stoker/Sloped Grate/Other | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | ppm at 3%O2
CO Biomass FB | NA | NA | 180 | 310 | 1.7222 | NA | NA | 180 | 310 | 1.7222 | ppm at 3%O2
CO Biomass Fuel Cell | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | ppm at 3%O2
CO Biomass Suspension Burner | NA | NA | 1400 | 2000 (10 day) | 1.4286 | NA | NA | 1400 | 2000 (10 day) | 1.4286 | ppm at 3%O2
CO Biomass Dutch/Pile | NA | NA | 440 | 520 (10 day) | 1.1818 | NA | NA | 440 | 520 (10 day) | 1.1818 | ppm at 3%O2
CO Biomass Hybrid Suspension/ Grate | NA | NA | 730 | 900 | 1.2329 | NA | NA | 730 | 900 | 1.2329 | ppm at 3%O2
CO Coal stoker | NA | NA | 34 | 340 | 10 | NA | NA | 34 | 340 | 10 | ppm at 3%O2
FB with heat exchanger |  |  |  | 150 | NA |  |  |  | 150 | NA
CO Coal FB | NA | NA | 59 | 230 | 3.8983 | NA | NA | 59 | 230 | 3.8983 | ppm at 3%O2
CO Coal pulverized | NA | NA | 28 | 320 | 11.4286 | NA | NA | 28 | 320 | 11.4286 | ppm at 3%O2
CO Oil - Heavy | NA | NA | 18 | na | NA | NA | NA | 18 | na | NA | ppm at 3%O2
CO Oil - Light | NA | NA | 60 | na | NA | NA | NA | 60 | na | NA | 1 day block average
CO Oil non-continental | NA | NA | 91 | na | NA | NA | NA | 91 | na | NA | 3 hour rolling average
HAP/Fuel | Proposal | Final | Re-proposal | 2012-12-01 | Factor Better | Proposal | Final | Re-proposal | 2012-12-01 | Factor Better | Units | Output Based (lb/MMBtu steam output) - March 2011 to December 2012
| Existing Boilers |  |  |  |  | New Boilers | [5 empty] | Existing | 2012-12-01 | New | 2012-12-01
D/F Biomass stoker | 0.004 | 0.005 | work practice | work practice | NA | 5e-05 | 0.005 | work practice | work practice | NA | ng/dscm at 7%O2 | 4.4e-12 | work practice | 4.4e-12 | work practice
D/F Biomass FB | 0.004 | 0.02 | work practice | work practice | NA | 0.007 | 0.02 | work practice | work practice | NA | ng/dscm at 7%O2 | 1.8e-11 | work practice | 1.8e-11 | work practice
D/F Biomass Dutch Oven | 0.03 | 0.2 | work practice | work practice | NA | 0.03 | 0.2 | work practice | work practice | NA | ng/dscm at 7%O2 | 1.8e-10 | work practice | 1.8e-10 | work practice
D/F Biomass Suspension Burner | NA | NA | work practice | work practice | NA | NA | NA | work practice | work practice | NA | NA | NA | work practice | NA | work practice
D/F Biomass Fuel Cell | 0.02 | 4 | work practice | work practice | NA | 0.0005 | 0.003 | work practice | work practice | NA | ng/dscm at 7%O2 | 3.5e-09 | work practice | 2.86e-12 | work practice
D/F Biomass Hybrid Suspension/Grate | NA | 0.2 | work practice | work practice | NA | NA | 0.2 | work practice | work practice | NA | ng/dscm at 7%O2 | 1.8e-10 | work practice | 1.8e-10 | work practice
D/F Coal pulverized | 0.004 | 0.004 | work practice | work practice | NA | 0.002 | 0.003 | work practice | work practice | NA | ng/dscm at 7%O2 | 3.7e-12 | work practice | 2.8e-12 | work practice
D/F Coal stoker | 0.003 | 0.003 | work practice | work practice | NA | 0.003 | 0.003 | work practice | work practice | NA | ng/dscm at 7%O2 | 2.8e-12 | work practice | 2.8e-12 | work practice
D/F Coal FB | 0.002 | 0.002 | work practice | work practice | NA | 3e-05 | 0.002 | work practice | work practice | NA | ng/dscm at 7%O2 | 1.8e-12 | work practice | 1.8e-12 | work practice
D/F Oil | 0.002 | 4 | work practice | work practice | NA | 0.002 | 0.002 | work practice | work practice | NA | ng/dscm at 7%O2 | 9.2e-09 | work practice | 4.6e-12 | work practice
D/F Gas2 | 0.009 | 0.08 | work practice | work practice | NA | 0.009 | 0.08 | work practice | work practice | NA | ng/dscm at 7%O2 | 3.9e-11 | work practice | 4.1e-12 | work practice | Existing |  |  |  |  | New
| Proposal | Final | Re-proposal | 2012-12-01 | Factor Better | Proposal | Final | Re-proposal | 2012-12-01 | Factor Better | Units | Output Based (lb/MMBtu steam output) - March 2011 to December 2012 |  |  |  | TSM, lb/MMBtu | TSM, lb/MMBtu | TSM, lb/MMBtu | Factor Better | Output Based lb/MMBtu steam | TSM, lb/MMBtu | Output Based lb/MMBtu steam
| Existing Boilers |  |  |  |  | New Boilers | [5 empty] | Existing | 2012-12-01 | New | 2012-12-01 | 2004 | Reprop | 2012-12-01 |  | 2012-12-01 | 2012-12-01 | 2012-12-01
PM Biomass Wet Stoker/Sloped Grate/Other | 0.02 | 0.039 | 0.029 | 0.037 | 1.2759 | lb/MMBtu | 0.001 | 0.029 | 0.03 | 1.0345 | lb/MMBtu | 0.35 | 0.043 | 0.13 | 0.035 | 0.001 | 5.7e-05 | 0.00024 | 4.2105 | 0.00028 | 2.6e-05 | 2.7e-05
PM Biomass Kiln-Dried Stoker/Sloped Grate/Other | 0.02 | 0.039 | 0.32 | 0.32 | 1 | lb/MMBtu | 0.001 | 0.32 | 0.03 | 0.09375 | lb/MMBtu | 0.35 | 0.37 | 0.13 | 0.035 | 0.001 | 0.004 | 0.004 | 1 | 0.0046 | 0.004 | 0.0042
PM Biomass FB | 0.02 | 0.039 | 0.11 | 0.11 | 1 | lb/MMBtu | 0.001 | 0.0098 | 0.0098 | 1 | lb/MMBtu | 0.28 | 0.14 | 0.18 | 0.012 | 0.001 | 0.0012 | 0.0012 | 1 | 0.0015 | 8.3e-05 | 0.00011
PM Biomass Dutch/Pile | 0.02 | 0.039 | 0.036 | 0.28 | 7.7778 | lb/MMBtu | 0.001 | 0.036 | 0.0032 | 0.088889 | lb/MMBtu | 0.45 | 0.39 | 0.45 | 0.0043 | 0.001 | 0.00024 | 0.002 | 8.3333 | 0.0028 | 3.9e-05 | 5.2e-05
PM Biomass Suspension Burner | 0.02 | 0.039 | 0.051 | 0.051 | 1 | lb/MMBtu | 0.001 | 0.051 | 0.03 | 0.58824 | lb/MMBtu | 0.45 | 0.052 | 0.45 | 0.031 | 0.001 | 0.0011 | 0.0065 | 5.9091 | 0.066 | 0.0065 | 0.0066
PM Biomass Fuel Cell | 0.02 | 0.039 | 0.033 | 0.02 | 0.60606 | lb/MMBtu | 0.001 | 0.011 | 0.02 | 1.8182 | lb/MMBtu | 0.34 | 0.055 | 0.23 | 0.03 | 0.001 | 4.9e-05 | 0.0058 | 118.3673 | 0.016 | 2.9e-05 | 5.1e-05
PM Biomass Hybrid Suspension/ Grate | 0.02 | 0.039 | 0.44 | 0.44 | 1 | lb/MMBtu | 0.001 | 0.026 | 0.026 | 1 | lb/MMBtu | 2 | 0.55 | 0.84 | 0.033 | 0.001 | 0.00049 | 0.00045 | 0.91837 | 0.00057 | 0.00044 | 0.00055
PM Coal pulverized | 0.02 | 0.039 | 0.044 | 0.04 | 0.90909 | lb/MMBtu | 0.001 | 0.0013 | 0.0011 | 0.84615 | lb/MMBtu | 0.14 | 0.042 | 0.01 | 0.0011 | 0.001 | 5.9e-05 | 5.3e-05 | 0.89831 | 5.6e-05 | 2.3e-05 | 2.7e-05
PM Coal stoker | 0.02 | 0.039 | 0.028 | 0.04 | 1.4286 | lb/MMBtu | 0.001 | 0.028 | 0.0011 | 0.039286 | lb/MMBtu | 0.25 | 0.042 | 0.005 | 0.0011 | 0.001 | 8.3e-05 | 5.3e-05 | 0.63855 | 5.6e-05 | 2.3e-05 | 2.7e-05
PM Coal FB | 0.02 | 0.039 | 0.088 | 0.04 | 0.45455 | lb/MMBtu | 0.001 | 0.0011 | 0.0011 | 1 | lb/MMBtu | 0.08 | 0.042 | 0.02 | 0.0011 | 0.001 | 1.7e-05 | 5.3e-05 | 3.1176 | 5.6e-05 | 2.3e-05 | 2.7e-05
PM Oil - heavy | 0.004 | 0.0075 | 0.062 | 0.062 | 1 | lb/MMBtu | 0.0013 | 0.013 | 0.013 | 1 | lb/MMBtu | 0.0083 | 0.075 | 0.0026 | 0.015 |  |  | 0.0002 | NA | 0.00025 | 7.5e-05 | 8.2e-05
PM Oil - light | 0.004 | 0.0075 | 0.0034 | 0.0079 | 2.3235 | lb/MMBtu | 0.0013 | 0.0011 | 0.0011 | 1 | lb/MMBtu | 0.0083 | 0.0096 | 0.0026 | 0.0012 |  |  | 6.2e-05 | NA | 7.5e-05 | 2.9e-05 | 3.2e-05
PM Oil non-continental | 0.004 | 0.0075 | 0.008 | 0.27 | 33.75 | lb/MMBtu | 0.0013 | 0.008 | 0.023 | 2.875 | lb/MMBtu | 0.13 | 0.33 | 0.043 | 0.025 |  |  | 0.00086 | NA | 0.0011 | 0.00086 | 0.00094
PM Gas2 | 0.05 | 0.043 | 0.0067 | 0.0067 | 1 | lb/MMBtu | 0.0067 | 0.0067 | 0.0067 | 1 | lb/MMBtu | 0.005 | 0.012 | 0.002 | 0.012 | NA | 0.00024 | 0.00021 | 0.875 | 0.00035 | 0.00021 | 0.00035
Follow work practices during periods of startup and shutdown. Startup and Shutdown are defined, work practice requirements are specified.