## ERU CISWIvsBlr
Comparison of Emission Limits between CISWI and Major Boiler Rules
| Major Boiler Limits |  |  |  |  | CISWI Limits for ERUs |  |  |  |  | CISWI Limits for ERUs
HAP/Fuel | Final | Final | Units | Output Based (lb/MMBtu steam output) |  | Final | Final | Units | Higher | Higher | Pollutant (units) 1 | Existing Units |  |  | New Sources
| Existing | New |  | Existing | New | Existing | New |  | Existing | New |  | Final |  |  | Final
Hg Biomass | 4.6 | 3.5 | lb/TBtu | 4.5e-06 | 3.4e-06 | 0.28625 | 0.28625 | lb/TBtu | MACT | MACT |  | Biomass | Coal | Liq/Gas | Biomass | Coal | Liq/Gas
PM Biomass | 0.039 | 0.0011 | lb/MMBtu | 0.038 | 0.0011 | 0.21686 | 0.21686 | lb/MMBtu | CISWI | CISWI | HCl (ppmv) | 0.45 | 0.45 | 14 | 0.45 | 0.45 | 14
HCl Biomass | 0.035 | 0.0022 | lb/MMBtu | 0.04 | 0.0021 | 0.00059365 | 0.00059365 | lb/MMBtu | MACT | MACT | CO (ppmv) | 490 | 59 | 36 | 160 | 46 | 36
[11 empty] | Pb (mg/dscm) | 0.0036 | 0.0036 | 0.096 | 0.002 | 0.002 | 0.096
Hg Coal | 4.6 | 3.5 | lb/TBtu | 4.5e-06 | 3.4e-06 | 0.30298 | 0.30298 | lb/TBtu | MACT | MACT | Cd (mg/dscm) | 0.00051 | 0.00051 | 0.023 | 0.00051 | 0.00051 | 0.023
PM Coal | 0.039 | 0.0011 | lb/MMBtu | 0.038 | 0.0011 | 0.22953 | 0.22953 | lb/MMBtu | CISWI | CISWI | Hg (mg/dscm) | 0.00033 | 0.00033 | 0.0013 | 0.00033 | 0.00033 | 0.00025
HCl Coal | 0.035 | 0.0022 | lb/MMBtu | 0.04 | 0.0021 | 0.00062834 | 0.00062834 | lb/MMBtu | MACT | MACT | PM filterable (mg/dscm) | 250 | 250 | 110 | 250 | 250 | 110
[11 empty] | Dioxin/Furans total (ng/dscm) OR | 0.35 | 0.35 | 2.9 | 0.068 | 0.068 | no limit
Hg Oil | 3.5 | 0.21 | lb/TBtu | 3.3e-06 | 2e-07 | 1.1216 | 0.21568 | lb/TBtu | MACT | CISWI | Dioxin/Furans TEQ (ng/dscm) | 0.059 | 0.059 | 0.32 | 0.011 | 0.011 | 0.002
Hg Oil non-continental | 0.78 | 0.78 | lb/TBtu | 8e-07 | 8e-07 | 1.1216 | 0.21568 | lb/TBtu | CISWI | MACT | NOX (ppmv) | 290 | 340 | 76 | 290 | 340 | 76
PM Oil | 0.0075 | 0.0013 | lb/MMBtu | 0.0073 | 0.001 | 0.094901 | 0.094901 | lb/MMBtu | CISWI | CISWI | SO2 (ppmv) | 6.2 | 650 | 720 | 6.2 | 650 | 720
HCl Oil | 0.00033 | 0.00033 | lb/MMBtu | 0.003 | 0.003 | 0.018369 | 0.018369 | lb/MMBtu | CISWI | CISWI | 1 All emission limits are measured at 7% oxygen.
ppmv = parts per million by volume.
Hg Gas 2 | 13 | 7.9 | lb/TBtu | 7.8e-06 | 2e-07 | 1.063 | 0.20442 | lb/TBtu | MACT | MACT | mg/dscm = milligrams per dry standard cubic meter.
PM Gas 2 | 0.043 | 0.0067 | lb/MMBtu | 0.026 | 0.004 | 0.089944 | 0.089944 | lb/MMBtu | CISWI | CISWI | ng/dscm = nanograms per dry standard cubic meter.
HCl Gas 2 | 0.0017 | 0.0017 | lb/MMBtu | 0.001 | 0.003 | 0.01741 | 0.01741 | lb/MMBtu | CISWI | CISWI
CO Biomass stoker | 490 | 160 | ppm at 3%O2 | 0.35 | 0.13 | 631.0072 | 206.0432 | ppm at 3%O2 | CISWI | CISWI | [7 empty] | HCl conversion factor, using PV=nRT
CO Biomass FB | 430 | 260 | ppm at 3%O2 | 0.28 | 0.18 | 631.0072 | 206.0432 | ppm at 3%O2 | CISWI | MACT | [7 empty] | mg HCl/dscm gas = X g moles HCl / 10E06 g moles gas) * (36.5 g HCl/g mole HCl) * (1 g mole gas / 24 liter @ 68F (Std Temp))*(1000 mg/g)*(1000 l/dscm)
CO Biomass Dutch/ Suspension | 470 | 470 | ppm at 3%O2 | 0.45 | 0.45 | 631.0072 | 206.0432 | ppm at 3%O2 | CISWI | MACT | [7 empty] | mg/dscm HCl = ppm * | 1.5208
CO Biomass Fuel Cell | 690 | 470 | ppm at 3%O2 | 0.34 | 0.23 | 631.0072 | 206.0432 | ppm at 3%O2 | MACT | MACT
CO Biomass Hybrid Suspension/ Grate | 3500 | 1500 | ppm at 3%O2 | 2 | 0.84 | 631.0072 | 206.0432 | ppm at 3%O2 | MACT | MACT | [7 empty] | bituminous coal | 9780 | dscf/MMBTU
CO Coal pulverized | 160 | 12 | ppm at 3%O2 | 0.14 | 0.01 | 75.9784 | 59.2374 | ppm at 3%O2 | MACT | CISWI | [7 empty] | wood | 9240 | dscf/MMBTU
CO Coal stoker | 270 | 6 | ppm at 3%O2 | 0.25 | 0.005 | 75.9784 | 59.2374 | ppm at 3%O2 | MACT | CISWI | [7 empty] | oil | 9190 | dscf/MMBTU
CO Coal FB | 82 | 18 | ppm at 3%O2 | 0.08 | 0.02 | 75.9784 | 59.2374 | ppm at 3%O2 | MACT | CISWI | [7 empty] | gas | 8710 | dscf/MMBTU
CO Oil | 10 | 3 | ppm at 3%O2 | 0.0083 | 0.0026 | 46.3597 | 46.3597 | ppm at 3%O2 | CISWI | CISWI
CO Oil non-continental | 160 | 51 | ppm at 3%O2 | 0.13 | 0.043 | 46.3597 | 46.3597 | ppm at 3%O2 | MACT | MACT
CO Gas2 | 9 | 3 | ppm at 3%O2 | 0.005 | 0.002 | 46.3597 | 46.3597 | ppm at 3%O2 | CISWI | CISWI
D/F Biomass stoker | 0.005 | 0.005 | ng TEQ/dscm at 7%O2 | 4.4e-12 | 4.4e-12 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | CISWI | CISWI
D/F Biomass FB | 0.02 | 0.02 | ng TEQ/dscm at 7%O2 | 1.8e-11 | 1.8e-11 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | CISWI | MACT
D/F Biomass Dutch/ Suspension | 0.2 | 0.2 | ng TEQ/dscm at 7%O2 | 1.8e-10 | 1.8e-10 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | MACT | MACT
D/F Biomass Fuel Cell | 4 | 0.003 | ng TEQ/dscm at 7%O2 | 3.5e-09 | 2.86e-12 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | MACT | CISWI
D/F Biomass Hybrid Suspension/Grate | 0.2 | 0.2 | ng TEQ/dscm at 7%O2 | 1.8e-10 | 1.8e-10 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | MACT | MACT
D/F Coal pulverized | 0.004 | 0.003 | ng TEQ/dscm at 7%O2 | 3.7e-12 | 2.8e-12 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | CISWI | CISWI
D/F Coal stoker | 0.003 | 0.003 | ng TEQ/dscm at 7%O2 | 2.8e-12 | 2.8e-12 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | CISWI | CISWI
D/F Coal FB | 0.002 | 0.002 | ng TEQ/dscm at 7%O2 | 1.8e-12 | 1.8e-12 | 0.059 | 0.011 | ng TEQ/dscm at 7%O2 | CISWI | CISWI
D/F Oil | 4 | 0.002 | ng TEQ/dscm at 7%O2 | 9.2e-09 | 4.6e-12 | 0.32 | 0.002 | ng TEQ/dscm at 7%O2 | MACT | CISWI
D/F Gas2 | 0.08 | 0.08 | ng TEQ/dscm at 7%O2 | 3.9e-11 | 4.1e-12 | 0.32 | 0.002 | ng TEQ/dscm at 7%O2 | CISWI | MACT