## Sheet1
2015-09-02
Common Fuel/ Thermal Energy Equivalent Comparison1
Industrial and Commercial Applications
Fuel | Delivered Cost2 | Units3 | BTU/Unit4 | Conversion Efficiency5 | $/MMBtu Thermal Energy
Electricity | 0.1 | $/kwh | 3412.8 | 98% | 29.8994
No.2 Oil | 3 | $/Gal (139000 Btu) | 139000 | 84% | 25.6937
Residual Oil | 2.5 | $/Gal (152000 Btu) | 152000 | 84% | 19.5802
Cord Wood | 150 | $/cord (2600 lbs/cord) | 15600000 | 60% | 16.0256
Electric Heat Pump | 0.1 | $/KWh Above 20 Deg F | 3412.8 | 300% | 9.7672
Natural Gas | 0.5 | Therm (100000 Btu) | 100000 | 82% | 6.0976
Biomass (Wet)6 | 30 | $/Ton (4,500 Btu/lb) | 9000000 | 65% | 5.1282
Biomass (Dry)6 | 40 | $/Ton (6,000 Btu/lb) | 12000000 | 70% | 4.7619
Eastern Coal | 100 | $/Ton (12,500 Btu/lb) | 25000000 | 85% | 4.7059
Illinois Basin Coal | 70 | $/Ton (11,000 Btu/lb) | 22000000 | 85% | 3.7433
PRB Coal | 55 | $/Ton (8,700 Btu/lb) | 17400000 | 85% | 3.7187
Tire Derived Fuel (TDF)6 | 40 | $/Ton (13,500 Btu/lb) | 27000000 | 85% | 1.7429
1. All information is given for relative comparison purposes. Site specific information can be inserted to obtain more accurate comparisons for an individual site.
2. Costs are considered as delivered to the burner for conversion to usable energy
3. Units are presented as normally seen with a typical "As Received" Higher Heating Value energy content.
4. Btu per unit are given as typical. Site specific information can be inserted to obtain more accurate comparisons for the individual site.
5. Efficiency percentages given are typical for conventional boiler/heating systems including moisture and flue gas losses at a boiler exit temperature of around 350 degrees F. Site specific information can be added to obtain more accurate results.
6. Considered opportunity fuels including fuel at $15.00/ton plus transportation, processing, handling, and delivery costs to the furnace. Fuel costs can vary widely based on demand and local availability. In some cases the cost of the fuel could be "free".